## Slide 1: Thermal Energy Storage (TES) applied to Concentrated Solar Power (CSP) UCC501 – Part 2
Dr. Nicolas CALVET
Assistant Professor
Thermal energy Storage Group Leader
iEnergy Center
Department of Mechanical and Materials Engineering (MME)

## Slide 2
Parabolic trough Power tower
Concentrated Solar Power Technologies
Dr. Nicolas CALVET
TES applied to CSP
Notes: INDICE DE CADA APARTADO

## Slide 3
1. Solar intermitencies
3. Customer side
MW
50
40
30
20
10
0
0 2 4 6 8 10 12 14 16 18 20 22 24
Storage
Direct
Sun
2. Daily solar curve
Hybridation using fossil fuel
Discharge from storage
4. Reduce the electricity cost
TES applied to CSP
Dr. Nicolas CALVET
Needs in TES?

## Slide 4
Sensible Heat
Latent Heat
Chemical Energy
Methods
Physical processes
Chemical processes
All Operating CSP plants use
sensible heat storages
TES applied to CSP
How to store Thermal Energy?
Dr. Nicolas CALVET

## Slide 5
Sensible Heat
Latent Heat
Stored heat
Temperature
Stored heat
Temperature
How to store Thermal Energy?
TES applied to CSP
Dr. Nicolas CALVET

## Slide 6
Comparison Sensible & Latent Heat
TES applied to CSP
Dr. Nicolas CALVET
In relative mass In relative volume
Concrete
(15)
Concrete (11)
Inorganics PCM (1)
Organic PCM
(2.5)
Water (6)
Water
(4)
Organics
PCM
(1.25)
Inorganics PCM (1)
DT = 15 K
in sensible heat
Same Stored Energy

## Slide 7
Concentrated Solar Energy
Endothermic
Reactor
A + ΔHR  B + C
Thermochemical Storage System (TCS)
ΔHR
Exothermic
Reactor
B+C  A + ΔHR
Power Block
ΔHR
B
C
ΔHR
Storage
A
Charge
Discharge
TES applied to CSP
Very high storage density compared to sensible & Latent heat
Dr. Nicolas CALVET

## Slide 8
How to store Thermal Energy?
Dr. Nicolas CALVET
TES applied to CSP
Storage Fluid = Heat Transfer Fluid (HTF) Storage Fluid  Heat Transfer Fluid (HTF)
Tested Technologies
Commercial Technologies
Under Development
Under Research
Notes: INDICE DE CADA APARTADO

## Slide 9: Tested Technologies
TES applied to CSP
Dr. Nicolas CALVET

## Slide 10
Solar One, Mojave desert, CA, USA
(10 MWel , 1982-1988)
Rocks and sand, oil as the HTF
Tested Technologies
1.1. Active Direct Storage – Single Tank Oil Thermocline + Filler Materials
TES applied to CSP
Dr. Nicolas CALVET

## Slide 11
Tested Technologies
1.1. Active Direct Storage – Single Tank Oil Thermocline + Filler Materials
TES applied to CSP
Dr. Nicolas CALVET
Problem of thermal expansion between the charge and discharge

## Slide 12
TES applied to CSP
1. Tested Technologies
1.2. Active Direct Storage – Two-tank Oil Technology
Dr. Nicolas CALVET
SEGS 1
(Solar Energy Generating Systems)
Mojave desert, CA, USA
14 MWe, 3 h storage, 240 - 307 C
Destroyed by fire in 1999

## Slide 13
THEMIS, Targasone, France
(2.5 MWel, 1983-1986)
Solar two, Mojave desert, CA, USA
(12.4 Mwel,1995-1999)
TES applied to CSP
1. Tested Technologies
1.3. Active Direct Storage – Two-tank Molten Salt Technology
Dr. Nicolas CALVET

## Slide 14: Commercial Technologies
TES applied to CSP
Dr. Nicolas CALVET

## Slide 15
Andasol 1, 50 MWe, Granada, Spain
2008: Andasol 1, First commercial CSP plant with storage
28 500 tons of nitrate salts
(60% NaNO3, 40% KNO3)
7.5 h storage, 291-384 ºC
Tank: h= 14 m, D= 36 m
TES applied to CSP
2. Commercial Technologies
2.1. Indirect Two-tank Molten Salt Technology
Dr. Nicolas CALVET

## Slide 16
Dr. Nicolas CALVET
TES applied to CSP

## Slide 17
Preheater
Evaporator
Superheater
TES applied to CSP
Dr. Nicolas CALVET

## Slide 18
TES applied to CSP
Dr. Nicolas CALVET

## Slide 19
500-750 euros/tonne sel
Source: Herrmann 2004
TES applied to CSP
2. Commercial Technologies
2.1. Indirect Two-tank Molten Salt Technology
Andasol 1, 50 MWe, Granada, Spain

## Slide 20
Source: Juan Ignacio Burgaleta, Director of Sener
TES applied to CSP
Dr. Nicolas CALVET

## Slide 21
8000 tons of Solar salt
TES applied to CSP
Dr. Nicolas CALVET
Source: Juan Ignacio Burgaleta, Director of Sener

## Slide 22
TES applied to CSP
Dr. Nicolas CALVET
Source: Juan Ignacio Burgaleta, Director of Sener

## Slide 23
TES applied to CSP
Source: Juan Ignacio Burgaleta, Director of Sener
Dr. Nicolas CALVET

## Slide 24
Two-tank Molten salt system
Natural gas heater
Power block
Cooling towers
Water treatment
Salt/Steam heat exchanger
TES applied to CSP
Dr. Nicolas CALVET

## Slide 25
Water can be a problem
TES applied to CSP
Dr. Nicolas CALVET
Source: Juan Ignacio Burgaleta, Director of Sener

## Slide 26
Charge
Discharge
TES applied to CSP
Dr. Nicolas CALVET
Source: Juan Ignacio Burgaleta, Director of Sener

## Slide 27
TES applied to CSP
Dr. Nicolas CALVET
Source: Juan Ignacio Burgaleta, Director of Sener

## Slide 28
50 mn at 50 % P
25 MWh
Saturated Steam
40 bars 250°C
Steam storage
20-30 kWh/m3
100 €/kWh
PS10 plant, 11 MWe, Seville
Unpredictable
intermittencies
TES applied to CSP
Dr. Nicolas CALVET
2. Commercial Technologies
2.2. Saturated Steam Storage

## Slide 29: Under Development
TES applied to CSP
Dr. Nicolas CALVET

## Slide 30
3.1 Passive storage: High-temperature Concrete
 | Advantages | drawbacks
Concrete HT | Concrete cost 80 €/tons Easy implementation | Limited to 500 °C 10 years life time Heat exchanger lost Contained Water
TES applied to CSP
3. Under development
Dr. Nicolas CALVET
Source: Dr. Doerte Laing (DLR)

## Slide 31
TES applied to CSP
3.1 Passive storage: High-temperature Concrete
3. Under development
Dr. Nicolas CALVET
Source: Dr. Doerte Laing (DLR)

## Slide 32
390°C Charge 6h 330°C
350°C Discharge 6h 290°C
25 bar
TES applied to CSP
3. Under development
3.1 Passive storage: High-temperature Concrete
Dr. Nicolas CALVET
Source: Dr. Doerte Laing (DLR)

## Slide 33
Storage
~ 300 m
~ 100 m
storage unit
storage unit
storage unit
storage unit
Photo: Solar Millenium AG
Dr. Nicolas CALVET
TES applied to CSP
Source: Dr. Doerte Laing (DLR)

## Slide 34
Jüllich, Germany, 2010
Air as HTF
Porous solid ceramics as storage material
1.5 h storage (120 – 680 ºC)
9 MWh (size: 7m x 7m x 6m)
TES unit
TES applied to CSP
3.2 Passive storage: Regenerator Type Storage
3. Under development
Dr. Nicolas CALVET

## Slide 35
Demo-storage system (1MWh) with concrete superheater (left) and PCM-Storage (right)
in the water/steam test loop at the power plant Litoral of Endesa in Carboneras, Spain
PCM
8.5m3
14 tons of NaNO3
Tm=306 °C
700 kWh
Concrete
22m3
300 kWh
Evaporation of steam
Superheating of steam
3. Under development
3.3 Passive storage: Combined sensible & Latent heat TES for DSG
Dr. Nicolas CALVET
TES applied to CSP

## Slide 36
Dr. Nicolas CALVET
3. Under development
3.4 Passive storage: Cascade Latent Heat Storage (CLHS)
TES applied to CSP

## Slide 37: Under Research
TES applied to CSP
Dr. Nicolas CALVET

## Slide 38
TES unit
TES applied to CSP
4.1 Active storage: Fluidized Bed Sand Storage Concept
4. Under Research
Dr. Nicolas CALVET
Advantages | Drawbacks
Sand cost 40€/tons High efficiency | Fluidised bed sand storage Erosion of pipes 10% of CSP energy used

## Slide 39
4.2. Conventional Heat Transfer Fluid (HTF): Synthetic Oil
Upper temperature limitation | 
Parabolic trough technology | Therminol VP-1®
500 °C | 400 °C
Fire in the solar field of ANDASOL 1 on December 15th, 2009
So called Solar oil = (oxide diphenyl 73.5 % and biphenyl 26.5 %)
Dr. Nicolas CALVET
TES applied to CSP
4. Under Research

## Slide 40
THEMIS Central Receiver Plant,
Targasone, FRANCE
Preventing salt crystallization in pipes
Themis CRP in the 80’s:
double envelope with superheated steam
Solar Two CRP in the 90’s:
& Gemasolar nowadays
electric tracing
Conventional Molten salts | TMax | Freezing temperature
Hitec® (KNO3 , NaNO2 , NaNO3) | 535°C | 142°C
Solar salt (NaNO3 , KNO3) | 600°C | 220°C
4.3. Molten salts as HTF in Central Receiver Plants (CRP)
No oil-to-salt heat exchanger
Higher temperature limitation
Higher efficiency
High freezing point
Dr. Nicolas CALVET
TES applied to CSP
4. Under Research

## Slide 41
Two tanks molten salts
1580 tons of nitrate salts
(60% NaNO3, 40% KNO3)
8 h storage, 290 – 550 ºC
Archimede Plant
Priolo Gargallo, Sicily
5 MWel , 2010
Huge length of parabolic trough collectors (6.4 km) !!
Dr. Nicolas CALVET
TES applied to CSP
4. Under Research
4.3. Molten salts as HTF in Parabolic Trough Plants

## Slide 42
As a promising candidate: Hitec XL® molten salt (Ca(NO3)2, NaNO3, KNO3) nitrates mixture
Lower crystallization temperature
Therminol VP-1® price: 2.2 $/kg
Hitec XL® price: 1.19 $/kg
Nº | Compositions name | Components wt% |  | 
 |  | Ca(NO3)2 | NaNO3 | KNO3
1 | Coastal C. | 42 | 15 | 43
2 | S. St. Laurent | 30 | 24 | 46
3 | Sandia lab. | 45 | 11 | 44
4 | D. Kearney | 48 | 7 | 45
5 | Eutectic | 44 | 12 | 44
Dr. Nicolas CALVET
TES applied to CSP
4. Under Research
4.3. Formulate New Molten salts Compositions

## Slide 43
Laboratory equipments
Rheometer
Thermal Gravimetric Analyzer (TGA)
Differential Scanning Calorimeter (DSC)
Glove box
X-Ray Diffractions (XRD)
Dr. Nicolas CALVET
TES applied to CSP
4. Under Research
4.3. Formulate New Molten salts Compositions

## Slide 44
From powder components pure at 99%
Under pure nitrogen in a glove box
Balance precise at 10-4 g
Mix during half an hour with ball miller
(Ca(NO3)2, NaNO3, KNO3) salts mixture
Ball miller
Glove box
Nitrates components
Dr. Nicolas CALVET
TES applied to CSP
4. Under Research
4.3. Formulate New Molten salts Compositions

## Slide 45
200°C
500°C
Thermal stability
TGA
40°C - 700°C
At 20 K/min
Dr. Nicolas CALVET
TES applied to CSP

## Slide 46
* Measured at CIC Energigune with STA 449 F3 from NETZSCH Company
Dr. Nicolas CALVET
TES applied to CSP
Thermal stability

## Slide 47
200°C
500°C
Tm = 116°C
Thermal cycling (Composition Nº6 NREL)
Melting temperature
DSC
Hitec XL® is stable on all the range of temperature of parabolic trough
30°C - 500°C
At 20 K/min
Dr. Nicolas CALVET
TES applied to CSP

## Slide 48
Viscosity measurements
Rheometer
=> Important parameter to pump the salt
Dr. Nicolas CALVET
TES applied to CSP

## Slide 49
For more information about this work, please refer to this publication in the International Journal of Solar Energy Engineering
Dr. Nicolas CALVET
TES applied to CSP

## Slide 50: Under Research at MI
TES applied to CSP
Dr. Nicolas CALVET

## Slide 51
TES Research Group Activity
Dr. Nicolas CALVET
Laboratory scale
TES Materials development
Pre-commercial scale
TES Systems Development
Masdar Institute Solar Platform (MISP), 100 kWth
Thermal Properties Characterization Laboratory

## Slide 52
TES Research Group Objectives
Source: US DOE
Reduce significantly the cost of TES systems
Increase the working temperature up to 1000 C
Propose Sustainable TES Solutions
Dr. Nicolas CALVET
TES 24%
TES - 80%

## Slide 53
TES Research Group Current Structure
TCES
Postdoctoral Researchers
TES Group Leader – Dr. Nicolas Calvet
Students
SANDSTOCK
Alberto Crespo Iniesta
Miguel Diago Martinez
iWaste
Ms. Kholoud Al Naimi
NEST
Dr. Mathieu Martins
CSPonD2
Dr. Benjamin Grange
Open Positions:
2 Ph.D.
Projects
Research Engineer
Research Associate
Uver Villalobos
Dr. Thomas Delclos
Dr. Thomas Delclos
Dr. Thomas Delclos
Dr. Bruno Cardenas
Victor Gutierrez Perez
Victor Gutierrez Perez
CSD
Mahmoud Alzoubi (Ph.D)
Dr. Nicolas CALVET

## Slide 54
Heat Exchanger
1. Sand Particles Solar Receiver/TES system
Alberto Crespo Iniesta (M.Sc.), Miguel Diago Martinez (M.Sc.), Dr. Thomas Delclos, Pr. Tariq Shamim, Dr. Quentin Falcoz (PROMES).
In collaboration with
TES Research Group Activity
Dr. Nicolas CALVET
Notes: Following idea of sand hourglass
Remove sand and change capital letters

## Slide 55
Dr. Nicolas CALVET
Heat Exchanger
Hot Tank
Cold Tank
Beam Down Concentrator
1. Sand Particles Solar Receiver/TES system
Alberto Crespo Iniesta (M.Sc.), Miguel Diago Martinez (M.Sc.), Dr. Thomas Delclos, Pr. Tariq Shamim, Dr. Quentin Falcoz (PROMES).
=
+
+
1 single material
Direct heat collector
Heat transfer
Storage
material
TES Research Group Activity

## Slide 56
Dynamic Measurement Under Concentrated Flux
35 o
Position of thermocouples
Position of thermocouples
Hot tank
Insulation
Solar conical receiver
Conical distributor
Moving sand bed
Conical distributor
Solar conical receiver
TES Research Group Activity
Dr. Nicolas CALVET

## Slide 57
2. High-Temperature Concrete Storage
Dr. Mathieu Martins, Uver Villalobos, Dr. Peter Armstrong, Dr. Paal Bergan (NEST), Dr. Christopher Greiner (NEST).
Dr. Nicolas CALVET
BDOE current solar receiver
HTF: Synthetic Oil (Tmax = 393 C)
Oil loop + Air-cooling system
In collaboration with
Objective:
Test a 500 kWthh prototype in real conditions of solar radiation
Main features of NEST:
Scalable
Versatile
Low cost
Efficient
Durable and safe
TES Research Group Activity

## Slide 58
3. Industrial Waste Recycled as TES Materials
In collaboration with
Ms. Kholoud Al Naimi (M.Sc.), Dr. Thomas Delclos.
Dr. Nicolas CALVET
- Furnace slag (EAF & LF)
- Aluminum Dross
- Pot skimming
365,000 tons of slags produced per year in the UAE
Aluminum Dross
Thermal Stability
TES Research Group Activity

## Slide 59
Solar Receiver
On the ground
Objective:
Develop new Combined Solar Receiver/TES systems
Higher temperature
Higher efficiency
Dr. Nicolas CALVET
TES Research Group Activity

## Slide 60
4. CSPonD2
Dr. Benjamin Grange, Dr. Saif Saeed Al Mheiri, Pr. Tariq Shamim, Dr. Peter Armstrong, Dr. Thomas Delclos, Dr. Mamoun Medraj.
Pr. Alexander Slocum, Pr. David Trumper, Pr. Charles Forsberg, Dr. Tom McKrell, Dr. Danny Codd (MIT).
Dr. Nicolas CALVET
In collaboration with
TES Research Group Activity

## Slide 61: Thank You
Version 1
Dr. Nicolas CALVET
ncalvet@masdar.ac.ae